## Instructions for Use
Piping Sizes Calculation The Smartflex Pressure Drop Calculator allows to check that the product pipe size is adequate to the site conditions. It is a Microsoft excel spreadsheet that evaluates the fluid flow through the pipe and, consequently, the pressure drop along the pipe runs. When asked to activate/inactivate macro, click on “activate”. The sheets are locked, so only those cells (in green) which require data input are accessible. It is sufficient to compute the worst case scenario, for example: ?? the one with the longest piping runs; ?? the smallest pipe size; ?? the highest flow rates required. Pressure Systems The information to be entered in the calculator is as follows: ?? length of piping runs (in meters or feet); ?? number of dispensers & nozzles per dispenser; ?? fluid type (e.g. Diesel, Gasoline…); ?? nominal Pipe Size (Outside diameter); ?? STP power (in Horsepower)*; ?? nozzle flow rate (in litres/min or in gallons/min), usually 40/80 litres/min or 10/20 gallons/min; ?? tank & dispenser relative elevations (in meters or feet), from the bottom of the dispenser to the bottom of the tank. Once all the information has been entered, the tool calculates the total pressure drop** for the system (in meters/feet or bars/psi) and the maximum fluid speed in the pipe (in meters or feet) and plots the result in a chart. As long as the pink dot is below the pump curve and there is no warning regarding the maximum fluid speed, the chosen pipe diameter is adequate for the intended service. The pump curve plotted (supplied by the pump manufacturer) represents the pump capacity and the pink dot represents the simulated piping system scenario, or rather, how many meters or feets the pump shall be capable to provide, at that required total flow rate, so that the intended service is guaranteed. *It is the responsibility of the user to verify and compare the pump curve assumed in this spreadsheet to the one relative to the pump that will be used, in order to avoid inaccurate evaluations. ** The total computed pressure drop considers also the fitting pressure drop contribution. For example, in case of a terminating dispenser, the calculator already includes the pressure drop due to the elbow and in case of an intermediate dispenser the tee contribution is considered. Suction Systems The information to be entered in the calculator is as follows: ?? length of piping runs (in meters or feet); ?? number of dispensers & nozzles per dispenser; ?? fluid type (e.g. Diesel, Gasoline…); ?? nominal Pipe Size (Outside diameter); ?? nozzle flow rate (in litres/min or in gallons/min), usually 40/80 litres/min or 10/20 gallons/min; ?? tank & dispenser relative elevations (in meters or feet), from the bottom of the dispenser to the top of the tank. Once all the information has been entered, the tool calculates the total pressure drop** for the system (in meters/feet or bars/psi) and the maximum fluid speed in the pipe (in meters or feet) and does not plot the result in a chart, as happens with pressure systems. In this case, the chosen pipe diameter is adequate for the intended service if the cell (F17) near the first dispenser representation is green and there is no warning regarding the maximum fluid speed. If the cell is red and/or the maximum speed warning appears, then the pipe size chosen is unsuitable. The value of F17 cell represents the calculation of NPSH of the piping system: in particular, if the cell is green, it means that the calculated value of NPSH is ≥ NPSH of the pump (= 0.6 bar) and if the cell turns red, it means that the condition is not satisfied. ** The total computed pressure drop considers also the fitting pressure drop contribution. For example, in case of a terminating dispenser the calculator includes the pressure drop due to the elbow and in case of an intermediate dispenser the tee contribution is considered. Keep in mind that these calculations are only estimates and that NUPIGECO is not responsible for erroneous evaluations. This calculator shall not replace a professional engineer’s judgment or advice. The information generated by or included in this tool does not represent a guarantee or warranty for piping installations and cannot be guaranteed, as the conditions of use are beyond our control.

## Metric Suction
[5 empty] | 3 |  | 3 |  |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1
|  | vel | 1.2752 | m/s |  | 0.6376 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
|  | q | 0.0026667 | m3/s | q | 0.0013333 | m3/s |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
|  | Re | 169561.0642 |  |  | 84780.5321 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
|  | f | 0.016011 |  |  | 0.018455 |  |  | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  | #DIV/0!
|  | k | 2.5 |  |  | 2.2 |  |  | 2.2 |  | 2.2 |  | 2.2 |  | 2.2 |  | 2.2 |  | 2.2
| a) | DP friction | 8484.3439 |  |  | 325.9802 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
| b) | DP fittings | 1519.0214 |  |  | 334.1847 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
|  | Losses (a+b) | 10003.3653 | Pa |  | 660.1649 |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
|  |  | 160 | l/min |  | 80 | l/min |  | 0 | l/min | 0 | l/min | 0 | l/min | 0 | l/min | 0 | l/min | 0 | l/min
|  |  | 45 | m |  | 6 | m |  | 10 | m | 10 | m | 10 | m | 10 | m | 10 | m | 10 | m
|  |  | 8.2762 | NPSH (m) |  | 8.1861 | m |  | 8.1861 |  | 8.1861 |  | 8.1861 |  | 8.1861 |  | 8.1861 |  | 8.1861
|  |  | 60672.5827 |  |  | 60012.4178 |  |  | 60012.4178 |  | 60012.4178 |  | 60012.4178 |  | 60012.4178 |  | 60012.4178 |  | 60012.4178
[28 empty] | Riga Selezione densità | riga selezione diametro
| INPUT DATA | [26 empty] | 2 | 4
Fluid Type
| Pipe Nominal Size | [24 empty] | OD | ID | Densità | Viscosità dinamica
[24 empty] | 9 | TSMA32 | 0.032 | 0.0252 | 997 | 0.000978 | Water | Non dispensing
[21 empty] | OD | 0.063 | m | 6 | TSMA40 | 0.04 | 0.032 | 747.3 | 0.00029 | Gasoline | 1 Nozzle
[21 empty] | ID | 0.0516 | m |  | TSMA50 | 0.05 | 0.0406 | 798.8 | 0.000255 | Diesel | 2 Nozzles
[21 empty] | Length | 45 | m |  | TSMA63 | 0.063 | 0.0516
| HYDRAULIC | [23 empty] | TSMA90 | 0.09 | 0.0746
| Flow rate per nozzle | 40 | l/min | [21 empty] | TSMA110 | 0.11 | 0.0918
| Elevation (tank-dispenser) | 4 | m | [21 empty] | TSMA160 | 0.16 | 0.1344
OUTPUT
| Pressure losses | 10663.5302 | Pa
| Pressure losses | 0.10664 | bar
| Pressure losses | 1.4546 | m
| Pressure losses + elevation | 39987.5822 | Pa
| Pressure losses + elevation | 0.39988 | bar
| Pressure losses + elevation | 5.4546 | m
| Maximum fluid speed | 1.2752 | m/s
GEOMETRIC
| Density | 747.3 | kg/m3 |  |  | Pipe OD | 63 | mm
| Dynamic Viscosity | 0.00029 | Pa s |  |  | Wall Thickness | 5.7 | mm
| Abs. Roughness | 2e-06 | m |  |  | Pipe ID | 51.6 | mm
2
|  | 3/4 HP | 1 -1/2 HP | 2 x 3/4 HP | 2 x 1 - 1/2 HP | 3 HP | 5 HP |  |  | 1 -1/2 HP
1 | 0 | 28 | 33 | 28 | 33 | 30 | 36 |  | 0 | 33 | 160 | 5.4546
2 | 50 | 27.5 | 32.9 | 28 | 33 | 30 | 35.6 |  | 50 | 32.9
3 | 100 | 23.5 | 31.1 | 27.5 | 32.9 | 29.6 | 35.2 |  | 100 | 31.1
4 | 150 | 17.5 | 28 | 26 | 32.5 | 29 | 34.5 |  | 150 | 28
5 | 200 | 8 | 22.5 | 23.5 | 31.4 | 28.2 | 33.7 |  | 200 | 22.5
6 | 250 |  | 15.8 | 20.6 | 30.1 | 27.2 | 32.9 |  | 250 | 15.8
7 | 300 |  | 6.5 | 17.2 | 28 | 26 | 32.1 |  | 300 | 6.5
8 | 350 |  |  | 13 | 25.5 | 24.7 | 31.24 |  | 350 | 0
9 | 400 |  |  | 8 | 22.5 | 22.9 | 30.4 |  | 400 | 0
10 | 450 |  |  |  | 19 | 20.4 | 29.6 |  | 450 | 0
11 | 500 |  |  |  | 15.5 | 18.1 | 28.8 |  | 500 | 0
12 | 550 |  |  |  | 11.4 | 15.8 | 27.9 |  | 550 | 0
13 | 600 |  |  |  | 6.5 | 13.1 | 26.7 |  | 600 | 0
14 | 650 |  |  |  |  | 10.3 | 25.4 |  | 650 | 0
15 | 700 |  |  |  |  | 7.4 | 23.8 |  | 700 | 0
16 | 750 |  |  |  |  | 4.1 | 21.9 |  | 750 | 0
17 | 800 |  |  |  |  | 0 | 19.9 |  | 800 | 0
18 | 850 | [5 empty] | 17.8 |  | 850 | 0
19 | 900 | [5 empty] | 15.6 |  | 900 | 0
20 | 950 | [5 empty] | 13.2 |  | 950 | 0
21 | 1000 | [5 empty] | 10.4 |  | 1000 | 0
22 | 1050 | [5 empty] | 7.6 |  | 1050 | 0
3/4 HP
1 -1/2 HP
2 x 3/4 HP
2 x 1 - 1/2 HP
3 HP
5 HP

## Metric Pressure
[5 empty] | 2 |  | 1 |  |  | 1 |  |  | 1 |  |  | 1 |  | 1 |  |  | 1 |  |  | 1
|  | vel | 0.51495 | m/s |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  | 0 |  | 0 |  |  | 0
|  | q | 0.00066667 | m3/s | q | 0 | m3/s |  | 0 |  |  | 0 |  |  | 0 |  | 0 |  | 0 |  |  | 0
|  | Re | 53875.3135 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  | 0 |  | 0 |  |  | 0
|  | f | 0.02037 |  |  | #DIV/0! |  |  | #DIV/0! |  |  | #DIV/0! |  |  | #DIV/0! |  | #DIV/0! |  | #DIV/0! |  |  | #DIV/0!
|  | k | 4.2 |  |  | 2.2 |  |  | 2.2 |  |  | 2.2 |  |  | 2.2 |  | 2.2 |  | 2.2 |  |  | 2.2
| a) | DP friction | 2087.9038 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  | 0 |  | 0 |  |  | 0
| b) | DP fittings | 416.148 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  | 0 |  | 0 |  |  | 0
|  | Losses (a+b) | 2504.0519 | Pa |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  | 0 |  | 0 |  |  | 0
|  |  | 40 | l/min |  | 0 | l/min |  | 0 | l/min |  | 0 | l/min |  | 0 | l/min | 0 | l/min | 0 | l/min |  | 0 | l/min
|  |  | 42 | m |  | 10 | m |  | 10 | m |  | 10 | m |  | 10 | m | 10 | m | 10 | m |  | 10 | m
[32 empty] | Riga Selezione densità | riga selezione diametro
| INPUT DATA | [30 empty] | 2 | 3
Fluid Type
| Pipe Nominal Size | [28 empty] | OD | ID | Densità | Viscosità dinamica
[28 empty] | 9 | TSMA32 | 0.032 | 0.0252 | 997 | 0.000978 | Water | Non dispensing
| STP power | [23 empty] | OD | 0.05 | m | 6 | TSMA40 | 0.04 | 0.032 | 747.3 | 0.00029 | Gasoline | 1 Nozzle
[25 empty] | ID | 0.0406 | m |  | TSMA50 | 0.05 | 0.0406 | 798.8 | 0.000255 | Diesel | 2 Nozzles
[25 empty] | Length | 42 | m |  | TSMA63 | 0.063 | 0.0516
| HYDRAULIC | [27 empty] | TSMA90 | 0.09 | 0.0746
| Flow rate per nozzle | 40 | l/min | [25 empty] | TSMA110 | 0.11 | 0.0918
| Elevation (tank-dispenser) | 4 | m | [25 empty] | TSMA160 | 0.16 | 0.1344
OUTPUT
| Pressure losses | 2504.0519 | Pa
| Pressure losses | 0.025041 | bar
| Pressure losses | 0.34157 | m
| Pressure losses + elevation | 31828.1039 | Pa
| Pressure losses + elevation | 0.31828 | bar
| Pressure losses + elevation | 4.3416 | m
| Maximum fluid speed | 0.51495 | m/s
GEOMETRIC
| Density | 747.3 | kg/m3 |  |  | Pipe OD | 50 | mm
| Dynamic Viscosity | 0.00029 | Pa s |  |  | Wall Thickness | 4.7 | mm
| Abs. Roughness | 2e-06 | m |  |  | Pipe ID | 40.6 | mm
1
|  | 3/4 HP | 1 -1/2 HP | 2 x 3/4 HP | 2 x 1 - 1/2 HP | 2 HP | 2 x 2 HP | 3 HP | 5 HP |  |  | 3/4 HP
1 | 0 | 28 | 33 | 28 | 33 | 33 | 33 | 30 | 36 |  | 0 | 28 |  | 40 | 4.3416
2 | 50 | 27.5 | 32.9 | 28 | 33 | 33 | 33 | 30 | 35.6 |  | 50 | 27.5
3 | 100 | 23.5 | 31.1 | 27.5 | 32.9 | 32 | 33 | 29.6 | 35.2 |  | 100 | 23.5
4 | 150 | 17.5 | 28 | 26 | 32.5 | 30 | 32.8 | 29 | 34.5 |  | 150 | 17.5
5 | 200 | 8 | 22.5 | 23.5 | 31.4 | 27 | 32 | 28.2 | 33.7 |  | 200 | 8
6 | 250 |  | 15.8 | 20.6 | 30.1 | 24 | 31 | 27.2 | 32.9 |  | 250 | 0
7 | 300 |  | 6.5 | 17.2 | 28 | 19 | 30 | 26 | 32.1 |  | 300 | 0
8 | 350 |  |  | 13 | 25.5 | 12 | 28.5 | 24.7 | 31.24 |  | 350 | 0
9 | 400 |  |  | 8 | 22.5 | 0 | 27 | 22.9 | 30.4 |  | 400 | 0
10 | 450 |  |  |  | 19 |  | 25.5 | 20.4 | 29.6 |  | 450 | 0
11 | 500 |  |  |  | 15.5 |  | 24 | 18.1 | 28.8 |  | 500 | 0
12 | 550 |  |  |  | 11.4 |  | 21.5 | 15.8 | 27.9 |  | 550 | 0
13 | 600 |  |  |  | 6.5 |  | 19 | 13.1 | 26.7 |  | 600 | 0
14 | 650 | [5 empty] | 15.5 | 10.3 | 25.4 |  | 650 | 0
15 | 700 | [5 empty] | 12 | 7.4 | 23.8 |  | 700 | 0
16 | 750 | [5 empty] | 6 | 4.1 | 21.9 |  | 750 | 0
17 | 800 | [5 empty] | 0 | 0 | 19.9 |  | 800 | 0
18 | 850 | [7 empty] | 17.8 |  | 850 | 0
19 | 900 | [7 empty] | 15.6 |  | 900 | 0
20 | 950 | [7 empty] | 13.2 |  | 950 | 0
21 | 1000 | [7 empty] | 10.4 |  | 1000 | 0
22 | 1050 | [7 empty] | 7.6 |  | 1050 | 0
3/4 HP
1 -1/2 HP
2 x 3/4 HP
2 x 1 - 1/2 HP
2 HP
2 x 2 HP
3 HP
5 HP

## US Suction
[6 empty] | 3 |  |  | 3 |  |  |  | 1 |  |  | 1 |  |  | 1 |  |  | 1 |  |  | 1 |  |  |  | 1
| vel |  | 1.2067 |  | m/s |  | 0.60333 |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
| q |  | 0.0025233 |  | m3/s | q | 0.0012617 |  | m3/s |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
| Re |  | 195044.1449 |  |  |  | 97522.0724 |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
| f |  | 0.015577 |  |  |  | 0.017919 |  |  |  | #DIV/0! |  |  | #DIV/0! |  |  | #DIV/0! |  |  | #DIV/0! |  |  | #DIV/0! |  |  | #DIV/0!
| k |  | 2.5 |  |  |  | 2.2 |  |  |  | 2.2 |  |  | 2.2 |  |  | 2.2 |  |  | 2.2 |  |  | 2.2 |  |  | 2.2
a) | DP friction |  | 13376.646 |  |  |  | 461.6255 |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
b) | DP fittings |  | 1453.8472 |  |  |  | 319.8464 |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
| Losses (a+b) |  | 14830.4932 |  | Pa |  | 781.4718 |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
|  |  | 151.4 | 40 | gpm |  | 75.7 | 20 | gpm |  | 0 | 0 | gpm | 0 | 0 | gpm | 0 | 0 | gpm | 0 | 0 | gpm | 0 | 0 | gpm | 0 | 0 | gpm
|  |  | 76.1963 | 250 | ft |  | 9.1436 | 30 | ft |  | 9.1436 | 30 | ft | 9.1436 | 30 | ft | 9.1436 | 30 | ft | 9.1436 | 30 | ft | 9.1436 | 30 | ft | 9.1436 | 30 | ft
|  |  | 61285.8494 |  |  |  | 60504.3776 |  |  |  | 60504.3776 |  |  | 60504.3776 |  |  | 60504.3776 |  |  | 60504.3776 |  |  | 60504.3776 |  |  | 60504.3776
[37 empty] | Riga Selezione densità | riga selezione diametro
INPUT DATA | [36 empty] | 3 | 4
Fluid Type
Pipe Nominal Size | [34 empty] | OD | ID | Densità | Viscosità dinamica
[33 empty] | 9 | TSMA32 | 0.032 | 0.0252 | 997 | 0.000978 |  | Water | Non dispensing
[30 empty] | OD | 0.063 | m | 6 | TSMA40 | 0.04 | 0.032 | 747.3 | 0.00029 |  | Gasoline | 1 Nozzle
[30 empty] | ID | 0.0516 | m |  | TSMA50 | 0.05 | 0.0406 | 798.8 | 0.000255 |  | Diesel | 2 Nozzles
[30 empty] | Length | 76.1963 | m |  | TSMA63 | 0.063 | 0.0516
HYDRAULIC | [33 empty] | TSMA90 | 0.09 | 0.0746
Flow rate per nozzle | 37.85 | 10 | gpm | gpm | [29 empty] | TSMA110 | 0.11 | 0.0918
Elevation (tank-dispenser) | 3.0479 | 10 | ft | ft | [29 empty] | TSMA160 | 0.16 | 0.1344
OUTPUT
15611.965
Pressure losses | 0.15612 | 2.2637 | psi | psi
Pressure losses | 1.9923 | 6.5367 | ft | feet
39495.6224
Pressure losses + elevation | 0.39496 | 5.7269 | psi | psi
Pressure losses + elevation | 5.0401 | 16.5367 | ft | feet
Maximum fluid speed | 1.2067 | 3.9591 | m/s | ft/s
2
[35 empty] | 3/4 HP | 1 -1/2 HP | 2 x 3/4 HP | 2 x 1 - 1/2 HP | 3 HP | 5 HP |  |  | 1 -1/2 HP
[33 empty] | 1 | 0 | 92.5 | 103.75 | 92.5 | 102.75 | 98 | 118 |  | 0 | 103.75 | 151.4 | 40 | 16.5367
[33 empty] | 2 | 10 | 92.5 | 102.5 | 92.5 | 102.5 | 98 | 117 |  | 10 | 102.5
[7 empty] | GEOMETRIC | [25 empty] | 3 | 20 | 88.75 | 101.25 | 92.5 | 102.5 | 98 | 116 |  | 20 | 101.25
| 798.8 |  | kg/m3 |  |  |  | Pipe OD |  | 63 | mm | [22 empty] | 4 | 30 | 81.25 | 97.5 | 90 | 102.5 | 96 | 115 |  | 30 | 97.5
| 0.000255 |  | Pa s |  |  |  | Wall Thickness |  | 5.7 | mm | [22 empty] | 5 | 40 | 68.75 | 91.25 | 88 | 101.25 | 95 | 113 |  | 40 | 91.25
| 2e-06 |  | m |  |  |  | Pipe ID |  | 51.6 | mm | [22 empty] | 6 | 50 | 50 | 82.5 | 83.75 | 100 | 93 | 111 |  | 50 | 82.5
[33 empty] | 7 | 60 | 21.25 | 71.25 | 81.25 | 97.5 | 91 | 109 |  | 60 | 71.25
[33 empty] | 8 | 70 |  | 56.25 | 73.75 | 95 | 88 | 107 |  | 70 | 56.25
[33 empty] | 9 | 80 |  | 40 | 68.75 | 91.25 | 85 | 105 |  | 80 | 40
[33 empty] | 10 | 90 |  | 22.5 | 60 | 87.5 | 82 | 103 |  | 90 | 22.5
[33 empty] | 11 | 100 |  | 0 | 50 | 82.5 | 78 | 101 |  | 100 | 0
[33 empty] | 12 | 110 |  |  | 37.5 | 76.25 | 73 | 99 |  | 110 | 0
[33 empty] | 13 | 120 |  |  | 21.25 | 71.25 | 66 | 97 |  | 120 | 0
[33 empty] | 14 | 130 |  |  | 7 | 63.75 | 60.5 | 95 |  | 130 | 0
[33 empty] | 15 | 140 |  |  |  | 56.25 | 55 | 93 |  | 140 | 0
[33 empty] | 16 | 150 |  |  |  | 48.75 | 49 | 90 |  | 150 | 0
[33 empty] | 17 | 160 |  |  |  | 40 | 42 | 87 |  | 160 | 0
[33 empty] | 18 | 170 |  |  |  | 32.5 | 35 | 84 |  | 170 | 0
[33 empty] | 19 | 180 |  |  |  | 22.5 | 28 | 80 |  | 180 | 0
[33 empty] | 20 | 190 |  |  |  |  | 20 | 76 |  | 190 | 0
[33 empty] | 21 | 200 |  |  |  |  | 12 | 71 |  | 200 | 0
[33 empty] | 22 | 210 |  |  |  |  | 0 | 66 |  | 210 | 0
[33 empty] | 23 | 220 | [5 empty] | 61 |  | 220 | 0
[33 empty] | 24 | 230 | [5 empty] | 55 |  | 230 | 0
[33 empty] | 25 | 240 | [5 empty] | 50 |  | 240 | 0
[33 empty] | 26 | 250 | [5 empty] | 44 |  | 250 | 0
[33 empty] | 27 | 260 | [5 empty] | 37 |  | 260 | 0
[33 empty] | 28 | 270 | [5 empty] | 30 |  | 270 | 0
[33 empty] | 29 | 280 | [5 empty] | 23 |  | 280 | 0
[33 empty] | 30 | 290 | [5 empty] | 16 |  | 290 | 0
[33 empty] | 31 | 300 | [5 empty] | 9 |  | 300 | 0
3/4 HP
1 -1/2 HP
2 x 3/4 HP
2 x 1 - 1/2 HP
3 HP
5 HP

## U.S. Pressure
[6 empty] | 3 |  |  | 3 |  |  |  | 1 |  |  | 1 |  |  | 1 |  |  | 1 |  |  |  | 1 |  |  |  | 1
| vel |  | 0.57731 |  | m/s |  | 0.28865 |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  | 0
| q |  | 0.0025233 |  | m3/s | q | 0.0012617 |  | m3/s |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  | 0
| Re |  | 110979.5349 |  |  |  | 55489.7674 |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  | 0
| f |  | 0.017444 |  |  |  | 0.020236 |  |  |  | #DIV/0! |  |  | #DIV/0! |  |  | #DIV/0! |  |  | #DIV/0! |  |  | #DIV/0! |  |  |  | #DIV/0!
| k |  | 2.5 |  |  |  | 2.2 |  |  |  | 2.2 |  |  | 2.2 |  |  | 2.2 |  |  | 2.2 |  |  | 2.2 |  |  |  | 2.2
a) | DP friction |  | 2218.7545 |  |  |  | 77.2196 |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  | 0
b) | DP fittings |  | 311.3287 |  |  |  | 68.4923 |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  | 0
| Losses (a+b) |  | 2530.0832 |  | Pa |  | 145.7119 |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  | 0
|  |  | 151.4 | 40 | gpm |  | 75.7 | 20 | gpm |  | 0 | 0 | gpm | 0 | 0 | gpm | 0 | 0 | gpm | 0 | 0 | gpm | 0 | 0 | gpm |  | 0 | 0 | gpm
|  |  | 76.1963 | 250 | ft |  | 9.1436 | 30 | ft |  | 9.1436 | 30 | ft | 9.1436 | 30 | ft | 9.1436 | 30 | ft | 9.1436 | 30 | ft | 9.1436 | 30 | ft |  | 9.1436 | 30 | ft
[38 empty] | Riga Selezione densità | riga selezione diametro
INPUT DATA | [37 empty] | 2 | 5
Fluid Type
Pipe Nominal Size | [35 empty] | OD | ID | Densità | Viscosità dinamica
[34 empty] | 9 | TSMA32 | 0.032 | 0.0252 | 997 | 0.000978 |  | Water | Non dispensing
STP power | [30 empty] | OD | 0.09 | m | 6 | TSMA40 | 0.04 | 0.032 | 747.3 | 0.00029 |  | Gasoline | 1 Nozzle
[31 empty] | ID | 0.0746 | m |  | TSMA50 | 0.05 | 0.0406 | 798.8 | 0.000255 |  | Diesel | 2 Nozzles
[31 empty] | Length | 76.1963 | m |  | TSMA63 | 0.063 | 0.0516
HYDRAULIC | [34 empty] | TSMA90 | 0.09 | 0.0746
Flow rate per nozzle | 37.85 | 10 | gpm | gpm | [30 empty] | TSMA110 | 0.11 | 0.0918
Elevation (tank-dispenser) | 3.0479 | 10 | ft | ft | [30 empty] | TSMA160 | 0.16 | 0.1344
OUTPUT
2675.7951
Pressure losses | 0.026758 | 0.38799 | psi | psi
Pressure losses | 0.365 | 1.1976 | ft | feet
25019.6323
Pressure losses + elevation | 0.2502 | 3.6278 | psi | psi
Pressure losses + elevation | 3.4128 | 11.1976 | ft | feet
Maximum fluid speed | 0.57731 | 1.8941 | m/s | ft/s
2
[36 empty] | 3/4 HP | 1 -1/2 HP | 2 x 3/4 HP | 2 x 1 - 1/2 HP | 2 HP | 2 x 2 HP | 3 HP | 5 HP |  | 1 -1/2 HP
[34 empty] | 1 | 0 | 92.5 | 103.75 | 92.5 | 102.75 | 109 | 109 | 98 | 118 | 0 | 103.75 | 151.4 | 40 | 11.1976
[34 empty] | 2 | 10 | 92.5 | 102.5 | 92.5 | 102.5 | 109 | 109 | 98 | 117 | 10 | 102.5
[7 empty] | GEOMETRIC | [26 empty] | 3 | 20 | 88.75 | 101.25 | 92.5 | 102.5 | 108.5 | 109 | 98 | 116 | 20 | 101.25
| 747.3 |  | kg/m3 |  |  |  | Pipe OD |  | 90 | mm | [23 empty] | 4 | 30 | 81.25 | 97.5 | 90 | 102.5 | 105 | 109 | 96 | 115 | 30 | 97.5
| 0.00029 |  | Pa s |  |  |  | Wall Thickness |  | 7.7 | mm | [23 empty] | 5 | 40 | 68.75 | 91.25 | 88 | 101.25 | 100 | 108.5 | 95 | 113 | 40 | 91.25
| 2e-06 |  | m |  |  |  | Pipe ID |  | 74.6 | mm | [23 empty] | 6 | 50 | 50 | 82.5 | 83.75 | 100 | 94 | 108 | 93 | 111 | 50 | 82.5
[34 empty] | 7 | 60 | 21.25 | 71.25 | 81.25 | 97.5 | 86 | 105 | 91 | 109 | 60 | 71.25
[34 empty] | 8 | 70 |  | 56.25 | 73.75 | 95 | 75 | 102.5 | 88 | 107 | 70 | 56.25
[34 empty] | 9 | 80 |  | 40 | 68.75 | 91.25 | 63 | 100 | 85 | 105 | 80 | 40
[34 empty] | 10 | 90 |  | 22.5 | 60 | 87.5 | 50 | 97 | 82 | 103 | 90 | 22.5
[34 empty] | 11 | 100 |  | 0 | 50 | 82.5 | 35 | 94 | 78 | 101 | 100 | 0
[34 empty] | 12 | 110 |  |  | 37.5 | 76.25 | 15 | 90 | 73 | 99 | 110 | 0
[34 empty] | 13 | 120 |  |  | 21.25 | 71.25 | 0 | 86 | 66 | 97 | 120 | 0
[34 empty] | 14 | 130 |  |  | 7 | 63.75 |  | 80.5 | 60.5 | 95 | 130 | 0
[34 empty] | 15 | 140 |  |  |  | 56.25 |  | 75 | 55 | 93 | 140 | 0
[34 empty] | 16 | 150 |  |  |  | 48.75 |  | 69 | 49 | 90 | 150 | 0
[34 empty] | 17 | 160 |  |  |  | 40 |  | 63 | 42 | 87 | 160 | 0
[34 empty] | 18 | 170 |  |  |  | 32.5 |  | 56.5 | 35 | 84 | 170 | 0
[34 empty] | 19 | 180 |  |  |  | 22.5 |  | 50 | 28 | 80 | 180 | 0
[34 empty] | 20 | 190 | [5 empty] | 42.5 | 20 | 76 | 190 | 0
[34 empty] | 21 | 200 | [5 empty] | 35 | 12 | 71 | 200 | 0
[34 empty] | 22 | 210 | [5 empty] | 25 | 0 | 66 | 210 | 0
[34 empty] | 23 | 220 | [5 empty] | 15 |  | 61 | 220 | 0
[34 empty] | 24 | 230 | [5 empty] | 8 |  | 55 | 230 | 0
[34 empty] | 25 | 240 | [5 empty] | 0 |  | 50 | 240 | 0
[34 empty] | 26 | 250 | [7 empty] | 44 | 250 | 0
[34 empty] | 27 | 260 | [7 empty] | 37 | 260 | 0
[34 empty] | 28 | 270 | [7 empty] | 30 | 270 | 0
[34 empty] | 29 | 280 | [7 empty] | 23 | 280 | 0
[34 empty] | 30 | 290 | [7 empty] | 16 | 290 | 0
[34 empty] | 31 | 300 | [7 empty] | 9 | 300 | 0
3/4 HP
1 -1/2 HP
2 x 3/4 HP
2 x 1 - 1/2 HP
2 HP
2 x 2 HP
3 HP
5 HP